## Slide 1: Desalination Technique

## Slide 2
Thermal Technology | Membrane Technology
Multi-Stage Flash Distillation (MSF) | Electrodialysis (ED
Vapor Compression Distillation (VCD) | Reverse Osmosis (RO)
THE MAJOR DESALINATION PROCESSES ARE IDENTIFIED
The two major types of technologies that are used around the world for desalination can be broadly classified as either thermal or membrane.
Both technologies need energy to operate and produce fresh water. Within those two broad types, there are sub-categories (processes) using different techniques. The major desalination processes are identified

## Slide 3: Reverse Osmosis – The Basics

## Slide 4
To understand RO’s purpose and process, first you must understand the naturally occurring process of Osmosis.
Osmosis is a naturally occurring phenomenon, and one of the most important processes in nature, where a weaker saline solution will tend to migrate to a strong saline solution. For example, when plant roots absorb water from the soil, or our kidneys absorb water from our blood.
The diagram to the right shows how osmosis works.
A less concentrated solution has a natural tendency to migrate to a solution with a higher concentration.
For example, if you had a container full of water with low salt concentration and another container full of water with high salt concentration, separated by a semi-permeable membrane, the water with the lower salt concentration would start to move towards the container with the higher salt concentration.

## Slide 5
A semi-permeable membrane allows some atoms or molecules to pass but not others. A simple example is a screen door which allows air molecules to pass through but not pests or anything larger than the screen holes.
Another example is Gore-Tex clothing which has an extremely thin plastic film with billions of small pores just big enough to let water vapor through, but small enough to prevent liquid water from passing.
Reverse Osmosis
RO is the process of Osmosis in reverse. Osmosis occurs naturally without an external energy source, but reversing the osmosis process requires applying energy to the more saline solution to reverse the natural flow.

## Slide 6: How does Reverse Osmosis work?
RO works using a high-pressure pump to apply pressure on the salt side of the RO system and to force the water across the semi- permeable RO membrane, leaving almost all (95% to 99%) of dissolved salts behind in the reject stream.
The amount of pressure required depends on the salt concentration of the feed water. The more concentrated the feed water, the more pressure is required to overcome the osmotic pressure.
Permeate vs. Concentrate Water:
In very simple terms, feed water is pumped into an RO system and two types of water come out: good water (permeate) and bad water (concentrate).
The “good” water has most contaminants removed and is called permeate. Another term for permeate is product water.

## Slide 7
As the feed water enters the RO membrane under pressure (enough to overcome osmotic pressure) the water molecules pass through the semi-permeable membrane and the salts and other contaminants remain on the other side and are discharged from the system through the concentrate stream.
The concentrate either goes to a drain or, in some circumstances, is fed back into the feed water supply and recycled through the RO system to save water. The water that makes it through the RO membrane usually has approximately 95% to 99% of dissolved salts removed.

## Slide 8: What is Reverse Osmosis Water?
Reverse osmosis water is purified water that has been filtered through a semipermeable membrane to remove dissolved salts, impurities, and contaminants. This process effectively eliminates minerals, chemicals, and other pollutants, producing clean, high-quality water.
RO can remove 95-99% of dissolved salts (ions), particles, colloids, organics, bacteria, and pyrogens from feed water. An RO membrane rejects contaminants based on their size and charge. Any contaminant with a molecular weight greater than 200 will likely be rejected by a properly running RO system.
The greater the ionic charge of the contaminant, the more likely it will be unable to pass through the RO membrane. For example, a sodium ion has only one charge (monovalent) and is not rejected by the RO membrane as well as calcium, which has two charges.

## Slide 9
RO systems cannot remove dissolved gases, such as carbon dioxide (CO2), very well because they are not highly ionized (charged) while in solution and have a very low molecular weight. Because RO systems do not remove gases, permeate water can have a slightly lower than normal pH level, depending on dissolved CO2 in the feed water since CO2 is converted to carbonic acid.
RO is very effective in treating brackish, surface and ground water for both large and small flow applications. Industries that use RO water include pharmaceutical, boiler feed water, food and beverage, metal finishing, and semiconductor manufacturing to name a few.

## Slide 10: RO systems performance and design calculations
There are a handful of calculations that are used to judge the performance of an RO system and for design considerations. An RO system has instrumentation that displays quality, flow, pressure and sometimes other data like temperature or hours of operation. To accurately measure the performance of an RO system you need the following operation parameters at a minimum:
Feed pressure
Permeate pressure
Concentrate pressure
Feed conductivity
Permeate conductivity
Concentrate flow
Permeate flow
Temperature

## Slide 11
Salt Rejection %
This equation tells you how effectively the RO membranes are removing contaminants. It does not tell you how each individual membrane is performing. However, it will tell you how the system overall is performing on average.
A well-designed RO system with properly functioning RO membranes will reject 95% to 99% of most feed water contaminants (of a certain size and charge).
The following equation can be used to determine how effective the RO membranes are at removing contaminants:
Salt Rejection % = ((Feed water conductivity – Permeate water conductivity) / Feed water conductivity) x 100

## Slide 12
Salt Passage %
This is simply the inverse of salt rejection described in the previous equation. This is the amount of salts, expressed as a percentage, passing through the RO system.
The lower the salt passage, the better the system is performing. A high salt passage can mean the membranes require cleaning or replacement.
Salt Passage % = (1 – Salt Rejection %) x 100
Recovery %
Recovery is the amount of feed water emerging from the system as good, permeate water.
Another way to think about recovery is as the amount of water collected as permeate or product water instead of being sent to drain as concentrate. Higher recovery percents mean you are sending less water to drain as concentrate and saving more permeate water. However, if recovery percents are too high for the RO design, it can lead to larger problems from membrane scaling and fouling.

## Slide 13
Design software establishes RO system recovery rates by considering numerous factors such as feed water chemistry and pre-treatment before the RO system. Therefore, proper RO system recovery depends on the design. Calculating the recovery facilitates rapid determination that the system is operating outside of the intended design.
The calculation below expresses the recovery rate as a percentage.
% Recovery= (Permeate Flow Rate gpm / (Permeate Flow Rate gpm + Concentrate Flow Rate gpm)) x 100
For example, if the recovery rate is 80% then for every 100 gallons of feed water entering the RO system, you are recovering 80 gallons as usable permeate water while 20 gallons go to the drain as concentrate.
Commercial RO systems typically run between 50% to 85% recovery depending on feed water characteristics and other design considerations.

## Slide 14: Concentration Factor
The concentration factor is related to RO system recovery and is important for RO system design. The more water you recover as permeate (higher recovery %), the more concentrated salts and contaminants you collect in the concentrate stream. When the concentration factor is too high for the system design and feed water composition, the system may experience increased scaling on RO membrane surfaces.
Concentration Factor = (1 / (1 – Recovery %)
The concept is no different than that of a boiler or cooling tower with purified water exiting the system as steam leaving a concentrated solution behind. As the concentration increases, solubility limits may be exceeded and precipitate on equipment surfaces as scale.

## Slide 15
For example, if your feed flow is 100 gpm and the permeate flow is 80 gpm, then the recovery is (80/100) x 100 = 80%.
To find the concentration factor, the formula would be 1 ÷ (1 – 80%) = 5.
A concentration factor of 5 means the water going to the concentrate stream will be 5 times more concentrated than the feed water. If the feed water in this example was 500 ppm, then the concentrate stream would be 500 x 5 = 2,500 ppm.
Flux Rate
Flux expresses the amount of water passing (permeating) through a reverse osmosis membrane during a given time, measured as gallons per square foot per day (GFD) or liters per square meter per hour (l/m²/hr).
A higher flux means more water is permeating through the RO membrane.

## Slide 16
Designers establish RO systems to operate within a specific flux range to ensure that the water flowing through the RO membrane is neither too fast nor too slow.
Flux Gfd = (Permeate flow gpm * 1,440) / (# of RO elements in system * square footage of each RO element)
For example, you have the following: The RO system is producing 80 gpm of permeate.(Gallons Per Minute)
The system has 3 RO vessels each holding 6 RO membranes for a total of 3 x 6 = 18 membranes.
The RO system membranes are Toray TMG20D-400 which has 400 square feet of surface area per membrane.

## Slide 17: Understanding the difference between passes and stages in a Reverse Osmosis (RO) system
The term ‘stage’ and ‘pass’ are often mistaken for the same thing in an RO system, and the terminology can be confusing for an RO operator. It is important to understand the difference between a one- and two-stage RO and a one- and two-pass RO.
1 stage vs 2 stage Reverse Osmosis (RO) system
In a one-stage RO system, the feed water enters as one stream and exits the RO as either concentrate or permeate water.
In a two-stage system, the concentrate (or reject) from the first stage then becomes feed water for the second stage.

## Slide 18
The permeate water collected from the first stage is combined with permeate water from the second stage. Additional stages increase the RO system’s recovery.

## Slide 19
References
https://puretecwater.com/resources/the-basics-of-reverseosmosis/#understandosmosis

## Slide 20
Reverse osmosis is the most widely used desalination technology, accounting for a significant portion of the world's desalinated water production. It involves the use of a semi permeable membrane that allows water molecules to pass through while rejecting dissolved salts and other impurities.

## Slide 21: Advantages of Reverse Osmosis Systems
Reverse osmosis filtration systems are among the most efficient methods for removing contaminants from water. They can effectively eliminate: Heavy metals such as lead, mercury, and arsenic.
Dissolved solids including salts from water and nitrates. Microorganisms such as bacteria, viruses, and parasites.Chemical impurities including fluoride, chlorine, and pesticides.
This ensures access to high-quality water that is entirely safe and free from harmful substances.

## Slide 22
Improves Taste & Odour
By removing contaminants, reverse osmosis water filtration systems improve the taste and odour of drinking water. Many people find that purified water tastes fresher and cleaner than untreated tap water. In most cases, untreated tap water can contain chlorine and other impurities.
Reduces Sodium & Hard Water Issues
RO systems are highly effective at reducing sodium and minerals from water. This makes them ideal for areas with hard water problems. This improves the efficiency of household appliances and extends their lifespan.

## Slide 23
Energy Efficient Compared to Distillation
Reverse osmosis is more energy-efficient than traditional distillation methods. While it does require energy to generate pressure for filtration, the overall energy consumption is lower compared to other water purification processes.
Versatility and Wide Applications
RO technology is used in various applications, including:
Residential Water Filtration: Providing safe drinking water for households.
Industrial Water Purification: Used in food processing, pharmaceuticals, and manufacturing industries.
Desalination of Seawater: Converting brackish water and seawater into potable water.
Agricultural Use: Ensuring high-quality water for irrigation and livestock.

## Slide 24: Disadvantages of Reverse Osmosis Systems Waste Water Generation
Waste Water Generation: One of the major drawbacks of reverse osmosis filtration systems is the generation of waste water. For every gallon of purified water produced, several gallons may be discarded as waste. This can be a concern in areas where water conservation is crucial.
Removes Beneficial Minerals: Reverse osmosis water filters not only remove contaminants from water. This also strips away beneficial minerals like calcium, magnesium, and potassium. The lack of essential minerals in RO water can lead to lower nutritional value and a bland taste.

## Slide 25
High Initial Cost & Maintenance
RO systems can be expensive to install, and ongoing maintenance costs include regular filter replacements and potential repairs. Some components, like the semi-permeable membrane, need to be replaced periodically. This is essential to maintain efficiency.
Environmental Concerns
The removal of minerals from water and the production of waste water can have environmental implications. Apart from that, discarded filters contribute to plastic waste, raising concerns about sustainability.

## Slide 26
Is Reverse Osmosis Water Safe for Drinking? Yes, reverse osmosis water is safe for drinking as it removes most harmful substances and provides purified water. However, because the process removes essential minerals, some users may prefer to add beneficial minerals back into the water using a remineralization filter.
How to Maintain a Reverse Osmosis System
To keep an RO system functioning efficiently, regular maintenance is necessary:
Change Filters Regularly: Pre-filters and post-filters should be replaced every 6-12 months.
Replace the RO Membrane: The semi-permeable membrane should be changed every 2-3 years. This can be based on water quality.
Sanitize the System Annually: This prevents bacterial growth and keeps the system clean.
Check for Leaks & Pressure Issues: Ensuring proper pressure helps to maintain filtration efficiency without any failure.

## Slide 27
Who Should Use Reverse Osmosis Filtration?
RO systems are a suitable option for:
Individuals in areas with contaminated water sources.
Households concerned about heavy metals and dissolved solids.
People looking for an alternative to bottled water.
Industrial applications where purified water is necessary.

## Slide 28
Conclusion
Reverse osmosis systems provide a highly effective solution for water purification. By removing contaminants from water, this system is essential to ensure safe drinking water. While they come with advantages like improved water quality and taste, they also have disadvantages, such as wastewater production and the removal of healthy minerals.
Understanding the advantages and disadvantages of reverse osmosis can help you to make a better decision according to your specific requirement. For those looking for high-quality, filtered water, an RO system remains one of the best membrane technologies available today.
As a top water treatment plant manufacturer, Alantech can help you find the right water purification plant. With over 12 years of industrial experience and a dedicated team, Alantech has completed over 500 installations successfully.